## Instrument Comparison
TIA Portal DB Instrument Status Comparison — PP
|  |  |  | PP 450 | [15 empty] | PP 750
Tag Label | Function | Unit | EM Module | Excel Val | Type (NC/NO) | Exp EN | Exp EX | Exp VF | Exp NO | Exp FBOPN_EN | Exp FBCLS_EN | DB EN | DB EX | DB VF | DB NO | DB FBOPN_EN | DB FBCLS_EN | Match | Action | Excel Val | Type (NC/NO) | Exp EN | Exp EX | Exp VF | Exp NO | Exp FBOPN_EN | Exp FBCLS_EN | DB EN | DB EX | DB VF | DB NO | DB FBOPN_EN | DB FBCLS_EN | Match | Action
AV201-1 | AV Valve | Unit Process | EM - 201 | X | NC | T | T | T | F | T | T | T | T | T | F | T | T | OK | OK | X | NC | T | T | T | F | T | T | T | T | T | F | T | T | OK | OK
AV208-1 | AV Valve | Unknown | EM - 208 | - | NC | F | F | F | F | F | F | F | F | T | F | T | T | DIFF | UPDATE: VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False | - | NC | F | F | F | F | F | F | F | F | T | F | T | T | DIFF | UPDATE: VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False
AV210-1 | AV Valve | Unknown | EM - 210 | - | NC | F | F | F | F | F | F | F | T | T | F | T | T | DIFF | UPDATE: EXIST: DB=True->False, VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False | - | NC | F | F | F | F | F | F | F | T | T | F | T | T | DIFF | UPDATE: EXIST: DB=True->False, VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False
AV212-1 | AV Valve | Unknown | EM - 212 | - | NO | F | F | F | T | F | F | F | T | T | T | T | T | DIFF | UPDATE: EXIST: DB=True->False, VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False | - | NO | F | F | F | T | F | F | F | T | T | T | T | T | DIFF | UPDATE: EXIST: DB=True->False, VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False
AV220-1 | AV Valve | Unit Process | EM - 22X | X | NC | T | T | T | F | T | T | T | T | T | F | T | T | OK | OK | X | NC | T | T | T | F | T | T | T | T | T | F | T | T | OK | OK
AV221-1 | AV Valve | Unit Process | EM - 22Y | X | NC | T | T | T | F | T | T | T | T | T | F | T | T | OK | OK | X | NC | T | T | T | F | T | T | T | T | T | F | T | T | OK | OK
AV222-1 | AV Valve | Unit Dch | EM - 222 | - | NC | F | F | F | F | F | F | F | T | T | F | T | T | DIFF | UPDATE: EXIST: DB=True->False, VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False | - | NC | F | F | F | F | F | F | F | T | T | F | T | T | DIFF | UPDATE: EXIST: DB=True->False, VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False
AV301-1 | AV Valve | Unit Dch | EM - 300 | X | NC | T | T | T | F | T | T | T | T | T | F | T | T | OK | OK | X | NC | T | T | T | F | T | T | T | T | T | F | T | T | OK | OK
AV320-1 | AV Valve | Unit Dch | EM - 300 | X | NC | T | T | T | F | T | T | T | T | T | F | T | T | OK | OK | X | NC | T | T | T | F | T | T | T | T | T | F | T | T | OK | OK
AV340-1 | AV Valve | Unit Process | EM - 340 | X | NC | T | T | T | F | T | T | T | T | T | F | T | T | OK | OK | X | NC | T | T | T | F | T | T | T | T | T | F | T | T | OK | OK
AV340-2 | AV Valve | Unit Process | EM - 340 | - | NC | F | F | F | F | F | F | F | T | T | F | T | T | DIFF | UPDATE: EXIST: DB=True->False, VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False | - | NC | F | F | F | F | F | F | F | T | T | F | T | T | DIFF | UPDATE: EXIST: DB=True->False, VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False
AV460-1 | AV Valve | Unit Process | EM - 22X | X | NO | T | T | T | T | T | T | T | T | T | T | T | T | OK | OK | X | NO | T | T | T | T | T | T | T | T | T | T | T | T | OK | OK
AV460-2 | AV Valve | Unit Process | EM - 340 | - | NO | F | F | F | T | F | F | F | T | T | T | T | T | DIFF | UPDATE: EXIST: DB=True->False, VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False | - | NO | F | F | F | T | F | F | F | T | T | T | T | T | DIFF | UPDATE: EXIST: DB=True->False, VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False
AV460d-1 | AV Valve | Unknown | EM - 460 | - | NO | F | F | F | T | F | F | F | T | T | T | T | T | DIFF | UPDATE: EXIST: DB=True->False, VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False | - | NO | F | F | F | T | F | F | F | T | T | T | T | T | DIFF | UPDATE: EXIST: DB=True->False, VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False
AV543-1 | AV Valve | Unit Dch | EM - 506 | - | NO | F | F | F | T | F | F | T | F | T | T | T | T | DIFF | UPDATE: ENABLE: DB=True->False, VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False | - | NO | F | F | F | T | F | F | T | F | T | T | T | T | DIFF | UPDATE: ENABLE: DB=True->False, VLV_W_FB: DB=True->False, FB_OPN_EN: DB=True->False, FB_CLS_EN: DB=True->False
AV463-1 | AV Valve | Unknown | EM - 463 | O | NO | T | F | T | T | T | T | F | T | T | T | T | T | DIFF | UPDATE: ENABLE: DB=False->True, EXIST: DB=True->False | O | NO | T | F | T | T | T | T | F | T | T | T | T | T | DIFF | UPDATE: ENABLE: DB=False->True, EXIST: DB=True->False
AV463-2 | AV Valve | Unknown | EM - 463 | O | NC | T | F | T | F | T | T | F | T | T | F | T | T | DIFF | UPDATE: ENABLE: DB=False->True, EXIST: DB=True->False | O | NC | T | F | T | F | T | T | F | T | T | F | T | T | DIFF | UPDATE: ENABLE: DB=False->True, EXIST: DB=True->False
AV461-1 | AV Valve | Unit Process | EM - 22Y | X | NO | T | T | T | T | T | T | T | T | T | T | T | T | OK | OK | X | NO | T | T | T | T | T | T | T | T | T | T | T | T | OK | OK
Tag Label | Function | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
FIS409-1 | COOLING LIQUID FLOW | Unit Sep | EM - 400 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
FIS615-1 | SEALING LIQUID FLOW INLET SEAL | Unit Sep | EM - 600 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
FIS635-1 | SEALING LIQUID FLOW OUTLET SEAL | Unit Sep | EM - 600 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
FIS630-1 | SEALING LIQUID FLOW OUTLET SEAL | Unit Sep | EM - 600 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
PIS340-1 | SAFETY LIQUID PRESSURE | Unit Process | EM - 340 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: ENABLE: DB=False->True
PIS375-1 | OP. LIQUID PRESSURE | Unit Dch | EM - 375 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
PS502-1 | INSTRUMENT AIR PRESSURE | Unit Sep | EM - 100 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
QT201-1_OK | HEALTHY STATUS | Unit Process | EM - 201 | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK
QT220-1_OK | HEALTHY STATUS | Unit Process | EM - 22X | O | - | T | F | N/A | - | N/A | N/A | T | F | N/A | F | N/A | N/A | OK | OK | O | - | T | F | N/A | - | N/A | N/A | T | F | N/A | F | N/A | N/A | OK | OK
QT220-2_OK | HEALTHY STATUS | Unknown | EM - 208 | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT FOUND IN DB | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT FOUND IN DB
eWON | eWON Talk2M STATUS | N/A | N/A | X | - | T | T | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | N/F | NOT IN DB MAP | X | - | T | T | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | N/F | NOT IN DB MAP
LA201-1 | INLET SIGHT GLASS BACKLIGHT | Unit Process | EM - 201 | - | - | F | F | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | DIFF | UPDATE: ENABLE: DB=True->False, EXIST: DB=True->False | - | - | F | F | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | DIFF | UPDATE: ENABLE: DB=True->False, EXIST: DB=True->False
LA220-1 | OUTLET SIGHT GLASS BACKLIGHT | Unit Process | EM - 22X | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
L-GREEN | SIGNAL TOWER-GREEN LIGHT | Unit Sep | EM - 100 | X | - | T | T | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: ENABLE: DB=False->True | X | - | T | T | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: ENABLE: DB=False->True
L-YELLOW | SIGNAL TOWER-YELLOW LIGHT | Unit Sep | EM - 100 | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
L-RED | SIGNAL TOWER-RED LIGHT/ALARM LIGHT | Unit Sep | EM - 100 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
L-BUZZ | SIGNAL TOWER-BUZZIER | Unit Sep | EM - 100 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
LA221-1 | OUTLET SIGHT GLASS BACKLIGHT | Unit Process | EM - 22Y | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
PIT201-1 | INLET PRESSURE | Unit Process | EM - 201 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
PIT22X-1 | SEPARATOR OUTLET 220 PRESSURE | Unit Process | EM - 22X | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
QT201-1 | INLET TURBIDITY | Unit Process | EM - 201 | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK
QT220-1 | OUTLET TURBIDITY | Unit Process | EM - 22X | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
QT220-2 | OUTLET TURBIDITY | Unknown | EM - 208 | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK
PIT22Y-1 | SEPARATOR OUTLET 221 PRESSURE | Unit Process | EM - 22Y | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
PIT222-1 | SOLIDS OUTLET PRESSURE | Unit Dch | EM - 222 | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK
LT-BT | BUFFER TANK LEVEL | N/A | N/A | O | - | T | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | N/F | NOT IN DB MAP | O | - | T | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | N/F | NOT IN DB MAP
LT463-1 | LEVEL IN B463-1 | Unknown | EM - 463 | O | - | T | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | DIFF | UPDATE: ENABLE: DB=False->True | O | - | T | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | DIFF | UPDATE: ENABLE: DB=False->True
PIT463-1 | E-MOTION PRESSURE | Unknown | EM - 463 | O | - | T | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | DIFF | UPDATE: ENABLE: DB=False->True | O | - | T | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | DIFF | UPDATE: ENABLE: DB=False->True
TT406-1 | COOLING LIQUID TEMPERATURE | Unknown | EM - 430 | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK
FIT201-1 | FEED FLOW | Unit Process | EM - 201 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
FIT208-1 | BLENDING FLOW | Unknown | EM - 208 | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK
FIT409-1 | COOLING LIQUID FLOW | Unit Sep | EM - 400 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
FCV201-1 | FEED FLOW | Unit Process | EM - 201 | O | NC | T | F | N/A | F | N/A | N/A | T | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | O | NC | T | F | N/A | F | N/A | N/A | T | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
PCV22X-1 | BACK PRESSURE 220 | Unit Process | EM - 22X | X | NO | T | T | N/A | T | N/A | N/A | T | T | N/A | F | N/A | N/A | DIFF | UPDATE: NO: DB=False->True | X | NO | T | T | N/A | T | N/A | N/A | T | T | N/A | F | N/A | N/A | DIFF | UPDATE: NO: DB=False->True
IP506A | DISCHARGE PRESSURE | N/A | N/A | X | NC | T | T | N/A | F | N/A | N/A | F | F | N/A | F | N/A | N/A | N/F | NOT IN DB MAP | X | NC | T | T | N/A | F | N/A | N/A | F | F | N/A | F | N/A | N/A | N/F | NOT IN DB MAP
PCV22Y-1 | BACK PRESSURE 221 | Unit Process | EM - 22Y | X | NO | T | T | N/A | T | N/A | N/A | T | T | N/A | T | N/A | N/A | OK | OK | X | NO | T | T | N/A | T | N/A | N/A | T | T | N/A | T | N/A | N/A | OK | OK
FCV208-1 | BLENDING FLOW | Unknown | EM - 208 | - | NC | F | F | N/A | F | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK | - | NC | F | F | N/A | F | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK
FCV210-1 | RECIRCULATION FLOW | Unknown | EM - 210 | - | NC | F | F | N/A | F | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK | - | NC | F | F | N/A | F | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK
FCV430-1 | GLYCOL FLOW | Unknown | EM - 430 | - | NC | F | F | N/A | F | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK | - | NC | F | F | N/A | F | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK
FCV409-1 | COOLING LIQUID FLOW CONTROL VALVE | Unit Sep | EM - 400 | X | NC | T | T | N/A | F | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | NC | T | T | N/A | F | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
ST74X | SPEED SENSOR PULSES | N/A | N/A | X | - | T | T | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | N/F | NOT IN DB MAP | X | - | T | T | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | N/F | NOT IN DB MAP
ST749 | SPEED SENSOR ALFDEX | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
EMS | E-STOP | Unit Sep | EM - 100 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
UPS | UPS BATTERY | Unit Sep | EM - 100 | X | - | T | T | N/A | - | N/A | N/A | T | F | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=False->True | X | - | T | T | N/A | - | N/A | N/A | T | F | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=False->True
P+F OS | OVERSPEED | Unit Sep | EM - 740 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
P+F ERROR | ERROR | Unit Sep | EM - 740 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
TS222-1 | SOLIDS PUMP TEMPERATURE | Unit Dch | EM - 222 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
TS730 | MOTOR WINDINGS TEMPERATURE | Unit Sep | EM - 730 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
LS222-1 | HIGH-HIGH LEVEL IN CYCLONE | Unit Dch | EM - 222 | O | - | T | F | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | O | - | T | F | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
LS222-2 | HIGH LEVEL IN CYCLONE | Unit Dch | EM - 222 | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK
LS222-3 | LOW LEVEL IN CYCLONE | Unit Dch | EM - 222 | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK
M701 | SEPARATOR VFD TRIP FB | Unit Sep | EM - 701 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
P222-1 | SOLIDS PUMP RUN FB | Unit Dch | EM - 222 | O | - | T | F | N/A | - | N/A | N/A | T | F | N/A | F | N/A | N/A | OK | OK | O | - | T | F | N/A | - | N/A | N/A | T | F | N/A | F | N/A | N/A | OK | OK
P403-1 | OIL COOLING PUMP RUN FB | Unknown | EM - 420 | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
P406-1 | COOLING RECIRC PUMP RUN FB | Unknown | EM - 430 | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
P463-1 | E-MOTION PUMP RUN FB | Unknown | EM - 463 | O | - | T | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: ENABLE: DB=False->True, EXIST: DB=True->False | O | - | T | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: ENABLE: DB=False->True, EXIST: DB=True->False
P201-1 | FEED PUMP RUN FB | Options | EM - P201 | O | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | O | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
P208-1 | BLENDING PUMP RUN FB | Unknown | EM - 208 | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
CA VIB WARN | COND.ALERT VIBRATION WARNING | Unit Sep | EM - 100 | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK
CA VIB ALM | COND.ALERT VIBRATION ALARM | Unit Sep | EM - 100 | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | OK
CA ERROR | CONDITION ALERT ERROR STATUS | Unit Sep | EM - 100 | - | NO | F | F | N/A | T | N/A | N/A | F | F | N/A | F | N/A | N/A | DIFF | UPDATE: NO: DB=False->True | - | NO | F | F | N/A | T | N/A | N/A | F | F | N/A | F | N/A | N/A | DIFF | UPDATE: NO: DB=False->True
CA WD | CONDITION ALERT WATCHDOG | Unit Sep | EM - 100 | - | NO | F | F | N/A | T | N/A | N/A | F | F | N/A | F | N/A | N/A | DIFF | UPDATE: NO: DB=False->True | - | NO | F | F | N/A | T | N/A | N/A | F | F | N/A | F | N/A | N/A | DIFF | UPDATE: NO: DB=False->True
FIS412-1 | COOLING LIQUID FLOW | Unit Sep | EM - 400 | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
FS421A | LUB OIL FLOW TOP BEARING | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
FS421B | LUB OIL FLOW BOTTOM BEARING | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
LS422a | HIGH LEVEL IN THE OIL TANK | Unknown | EM - 420 | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
LS42X(b) | LOW LEVEL IN THE OIL TANK | Unknown | EM - 420 | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
LS422-1 | WATER IN THE OIL TANK | Unknown | EM - 420 | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
PS503-1 | AIR PRESSURE V421 | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
P+F PS | POWER SUPPLY | Unit Sep | EM - 740 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
M701 AMP | AMPS SIGNAL ANALOGUE | N/A | N/A | X | - | T | T | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | N/F | NOT IN DB MAP | X | - | T | T | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | N/F | NOT IN DB MAP
YT75X | VIBRATIONS FRAME | Unit Sep | EM - 750 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
FIT412-1 | COOLING LOQUID FLOW | Unit Sep | EM - 400 | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
PT37X-1 | OP. LIQUID PRESSURE | Unit Dch | EM - 375 | O | - | T | F | N/A | - | N/A | N/A | T | F | N/A | F | N/A | N/A | OK | OK | O | - | T | F | N/A | - | N/A | N/A | T | F | N/A | F | N/A | N/A | OK | OK
TT730 | MOTOR TEMPERATURE | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
TT731 | TOP BEARING TEMPERATURE | N/A | N/A | X | - | T | T | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | N/F | NOT IN DB MAP | X | - | T | T | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | N/F | NOT IN DB MAP
TT731b/TT733 | GEAR OIL/TOP BEARING TEMPERATURE | N/A | N/A | X | - | T | T | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | N/F | NOT IN DB MAP | X | - | T | T | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | N/F | NOT IN DB MAP
TT222-1 | SOLIDS PUMP TEMPERATURE | Unit Dch | EM - 222 | O | - | T | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | DIFF | UPDATE: ENABLE: DB=False->True | O | - | T | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | DIFF | UPDATE: ENABLE: DB=False->True
TT411-1 | COOLING LIQUID TEMPERATURE | Unit Sep | EM - 400 | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
TT730b | ROTOR AIR TEMPERATURE | Unit Sep | EM - 730 | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
TT734 | BOTTOM BEARING TEMPERATURE | Unit Sep | EM - 730 | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | - | - | F | F | N/A | - | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
TT41X-1 | COOLING LIQUID TEMPERATURE | Unit Sep | EM - 400 | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
YT750b | VIBRATIONS FRAME | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
YT751 | VIBRATIONS TOP BEARING | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
ST740 | BOWL SPEED | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
VIB WARN | CA VIBRATION WARNING | N/A | N/A | - | NO | F | F | N/A | T | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | NO | F | F | N/A | T | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
VIB ALM | CA VIBRATION ALARM | N/A | N/A | - | NO | F | F | N/A | T | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | NO | F | F | N/A | T | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
AV302-1 | FLUSH OUTLET SEAL | Unit Dch | EM - 300 | - | NC | F | F | F | F | F | F | F | T | F | F | F | F | DIFF | UPDATE: EXIST: DB=True->False | - | NC | F | F | F | F | F | F | F | T | F | F | F | F | DIFF | UPDATE: EXIST: DB=True->False
AV303-1 | FLUSH UNDER THE BOWL | Unit Dch | EM - 300 | X | NC | T | T | F | F | F | F | T | T | F | F | F | F | OK | OK | X | NC | T | T | F | F | F | F | T | T | F | F | F | F | OK | OK
AV304-1 | FLUSH SOLIDS OUTLET | Unit Dch | EM - 300 | X | NC | T | T | F | F | F | F | T | T | F | F | F | F | OK | OK | X | NC | T | T | F | F | F | F | T | T | F | F | F | F | OK | OK
AV305-1 | FLUSH CYCLONE | Unit Dch | EM - 300 | X | NC | T | T | F | F | F | F | T | T | F | F | F | F | OK | OK | X | NC | T | T | F | F | F | F | T | T | F | F | F | F | OK | OK
AV306-1 | FLUSH CYCLONE PIPE | Unit Dch | EM - 300 | - | NC | F | F | F | F | F | F | F | T | F | F | F | F | DIFF | UPDATE: EXIST: DB=True->False | - | NC | F | F | F | F | F | F | F | T | F | F | F | F | DIFF | UPDATE: EXIST: DB=True->False
AV37X-1 | OP. LIQUID SUPPLY | Unit Dch | EM - 375 | X | NC | T | T | F | F | F | F | T | T | F | F | F | F | OK | OK | X | NC | T | T | F | F | F | F | T | T | F | F | F | F | OK | OK
AV409-1 | COOLING LIQUID SUPPLY | Unit Sep | EM - 400 | X | NC | T | T | F | F | F | F | T | T | F | F | F | F | OK | OK | X | NC | T | T | F | F | F | F | T | T | F | F | F | F | OK | OK
AV615-1 | SEALING LIQUID SUPPLY | Unit Sep | EM - 600 | X | NO | T | T | F | T | F | F | T | T | F | T | F | F | OK | OK | X | NO | T | T | F | T | F | F | T | T | F | T | F | F | OK | OK
AV635-1 | FLUSH MECHANICAL SEALS | Unit Dch | EM - 300 | X | NC | T | T | F | F | F | F | T | T | F | F | F | F | OK | OK | X | NC | T | T | F | F | F | F | T | T | F | F | F | F | OK | OK
AV63X/441-1 | SEALING LIQUID SUPPLY | Unit Sep | EM - 600 | - | NO | F | F | F | T | F | F | F | T | F | T | F | F | DIFF | UPDATE: EXIST: DB=True->False | - | NO | F | F | F | T | F | F | F | T | F | T | F | F | DIFF | UPDATE: EXIST: DB=True->False
AVDCH | OWMC DISCHARGE VALVE | Unit Dch | EM - 506 | X | NC | T | T | F | F | F | F | T | T | F | F | F | F | OK | OK | X | NC | T | T | F | F | F | F | T | T | F | F | F | F | OK | OK
SV503-1 | AIR SUPPLY LUBRICATION SYSTEM | N/A | N/A | - | NC | F | F | N/A | F | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | NC | F | F | N/A | F | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
PV421-1 | COOLING TOP BEARING | Unknown | EM - 420 | - | NC | F | F | F | F | F | F | F | T | F | F | F | F | DIFF | UPDATE: EXIST: DB=True->False | - | NC | F | F | F | F | F | F | F | T | F | F | F | F | DIFF | UPDATE: EXIST: DB=True->False
P421-1 | LUBRICATION PUMP | Unknown | EM - 420 | - | NC | F | F | N/A | F | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False | - | NC | F | F | N/A | F | N/A | N/A | F | T | N/A | F | N/A | N/A | DIFF | UPDATE: EXIST: DB=True->False
PV376-1 | OP. LIQUID SUPPLY OWMC | Unit Dch | EM - 506 | O | NC | T | F | F | F | F | F | T | F | F | F | F | F | OK | OK | O | NC | T | F | F | F | F | F | T | F | F | F | F | F | OK | OK
PV376-2 | OP. LIQUID SUPPLY OWMC | Unit Dch | EM - 506 | O | NO | T | F | F | T | F | F | T | F | F | F | F | F | DIFF | UPDATE: NO: DB=False->True | O | NO | T | F | F | T | F | F | T | F | F | F | F | F | DIFF | UPDATE: NO: DB=False->True
AV660-1 | E-MOTION | Unknown | EM - 463 | O | NC | T | F | F | F | F | F | F | T | F | F | F | F | DIFF | UPDATE: ENABLE: DB=False->True, EXIST: DB=True->False | O | NC | T | F | F | F | F | F | F | T | F | F | F | F | DIFF | UPDATE: ENABLE: DB=False->True, EXIST: DB=True->False
AV470-1 | E-MOTION | Unknown | EM - 463 | O | NO | T | F | F | T | F | F | F | T | F | T | F | F | DIFF | UPDATE: ENABLE: DB=False->True, EXIST: DB=True->False | O | NO | T | F | F | T | F | F | F | T | F | T | F | F | DIFF | UPDATE: ENABLE: DB=False->True, EXIST: DB=True->False
AV430-1 | GLYCOL SUPPLY | Unknown | EM - 430 | - | NC | F | F | F | F | F | F | F | T | F | F | F | F | DIFF | UPDATE: EXIST: DB=True->False | - | NC | F | F | F | F | F | F | F | T | F | F | F | F | DIFF | UPDATE: EXIST: DB=True->False
AV305-2 | E-MOTION | Unknown | EM - 463 | O | NC | T | F | F | F | F | F | F | T | F | F | F | F | DIFF | UPDATE: ENABLE: DB=False->True, EXIST: DB=True->False | O | NC | T | F | F | F | F | F | F | T | F | F | F | F | DIFF | UPDATE: ENABLE: DB=False->True, EXIST: DB=True->False
AV660-2 | E-MOTION | Unknown | EM - 463 | O | NC | T | F | F | F | F | F | F | T | F | F | F | F | DIFF | UPDATE: ENABLE: DB=False->True, EXIST: DB=True->False | O | NC | T | F | F | F | F | F | F | T | F | F | F | F | DIFF | UPDATE: ENABLE: DB=False->True, EXIST: DB=True->False
FIT22X-1 | VOLUME FLOW | Unit Process | EM - 22X | O | - | T | F | N/A | - | N/A | N/A | T | F | N/A | F | N/A | N/A | OK | OK | O | - | T | F | N/A | - | N/A | N/A | T | F | N/A | F | N/A | N/A | OK | OK
FIT22Y-1 | VOLUME FLOW | Unit Process | EM - 22Y | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK | X | - | T | T | N/A | - | N/A | N/A | T | T | N/A | F | N/A | N/A | OK | OK
SC701 CW | COMMAND WORD | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
SC701 REF | SPEED REFERENCE | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
SC701 SW | STATUS WORD | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
SC701 ACT | ACTUAL SPEED | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
SC701 AMPS | AMPS | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
P201-1 CW | COMMAND WORD | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
P201-1 REF | SPEED REFERENCE | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP
P201-1 SW | STATUS WORD | N/A | N/A | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP | - | - | F | F | N/A | - | N/A | N/A | F | F | N/A | F | N/A | N/A | OK | NOT IN DB MAP

## Summary
Family | OK | MISMATCH | NOT FOUND | mc_idx
PP 450 | 62 | 47 | 28 | 2
PP 750 | 61 | 48 | 28 | 3